## DRIVE
|  | DRIVEN EQUIPMENT | [6 empty] | CONDITIONS OF INSTALLATION |  |  |  | IEC MOTOR
Drive Nb |  | Name | Typ | Item | Operat. Speed | Coupling | Duty | Absorbed Power | Drive->Panel | Climatic Cond. | Corros | Operating temp [°] | Rated Power | Frame size | Rated Speed | Mounting | Painting | IP Rate | Cooling | Standard | Insulation | JB IP rate/ Pos °/ CG tape | Efficiency | Power | Rated Current [A] | Rated Voltage | Starting | Winding
[6 empty] | Type | service | [KW] | Lenght [m] |  | Category | Alti[m] | [KW] |  | [rpm] | Position |  |  | Method |  |  |  | IE3 at100% | Factor | Star-Delta-Line | Start [V]- Delta[V] | Methode | Protection
1 |  | Belt drive | Conveyor | - | 10…100Hz ( 1:10) | - | S1 | - | 150…300m | Inside -Non Atex | None | 10…40 / <1000m | 1.1 | 90 | 1762 | - | - | IP65/ TEFC | IC411 | IEC60034 | F/B | - | 93.6 IE3 | 0.85 | 2,2 / 3,85 -3x480 | 3x480-3x277 | Inverter | -
2 |  | Belt drive | Conveyor | - | 10…100Hz ( 1:10) | - | S1 | - | 150…300m | Inside -Non Atex | None | 10…40 / <1000m | 0.75 | 80 | 1751 | - | - | IP65/ TEFC | IC411 | IEC60034 | F/B | - | 91.5 IE3 | 0.81 | 1,5/ 2,6 -3x380V | 3x480-3x277 | Inverter | -
3 |  | Belt drive | Conveyor | - | 10…100Hz ( 1:10) | - | S1 | - | 150…300m | Inside -Non Atex | None | 10…40 / <1000m | 0,75 | 80 | 1751 | - | - | IP65/ TEFC | IC411 | IEC60034 | F/B | - | 90.6 IE3 | 0.81 | 1,5/ 2,6 -3x380V | 3x480-3x277 | Inverter | -
4 |  | Belt drive | Conveyor | - | 10…100Hz ( 1:10) | - | S1 | - | 150…300m | Inside -Non Atex | None | 10…40 / <1000m | 0,75 | 80 | 1751 | - | - | IP65/ TEFC | IC411 | IEC60034 | F/B | - | 90.6 IE3 | 0.81 | 1,5/ 2,6 -3x380V | 3x480-3x277 | Inverter | -
5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | IEC60034 | F/B | - | - | - | - | - | - | -
6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | IEC60034 | F/B | - | - | - | - | - | - | -
7 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | IEC60034 | F/B | - | - | - | - | - | - | -
CONSUMER DATA
|  | MOTOR |  |  |  | ELEC DEVICE ( TRANSFOR-PS-INVERTER-SOFT STARTER) | [8 empty] | LINE CURRENT
Drive Nb | Quantity | Consumer typ | Rated Power | Rated Current | Starting | Typ | Power | Output Current | Input Current | Power loss | Weight | Conduct Cross Sec | Power | Operat lenght | I L1 | I L2 | I L3 | Power | I L1 | I L2 | I L3
|  |  | [KW] | [A] 380V | Methode |  | [KW] | [A] 480V | [A] 480V | [W] | [kg] | In/Out | [VA] | [m] | [A] | [A] | [A] | [VA] | [A] | [A] | [A]
[7 empty] | LO/HO | LO/HO/Max | LO/HO |  |  | [mm2]
1 | 1 | Motor | 1.1 | 2,2 / 3,85 -3x480 | Inverter | 25B-D4P0N114 | 1,5/1,5 | 4,0/5,2 | 5,7/5,7 | 63 | - | - | 4800 | - | 5.7 | 5.7 | 5.7 | 4800 | 5.7 | 5.7 | 5.7
2 | 1 | Motor | 0.75 | 1,5/ 2,6 -3x380V | Inverter | 25B-D4P0N114 | 1,5/1,5 | 4,0/5,2 | 5,7/5,7 | 63 | - | - | 4800 | - | 5.7 | 5.7 | 5.7 | 4800 | 5.7 | 5.7 | 5.7
3 | 1 | Motor | 0,75 | 1,5/ 2,6 -3x380V | Inverter | 25B-D4P0N114 | 1,5/1,5 | 4,0/5,2 | 5,7/5,7 | 63 | - | - | 4800 | - | 5.7 | 5.7 | 5.7 | 4800 | 5.7 | 5.7 | 5.7
4 | 1 | Motor | 0,75 | 1,5/ 2,6 -3x380V | Inverter | 25B-D4P0N114 | 1,5/1,5 | 4,0/5,2 | 5,7/5,7 | 63 | - | - | 4800 | - | 5.7 | 5.7 | 5.7 | 4800 | 5.7 | 5.7 | 5.7
-
5 | 0 | Motor | - | - | - | - | - | - | - | - | - | - | 0 | - | 355 | 355 | 355 | 0 | 0 | 0 | 0
[5 empty] | Delta motor | -
6 | 0 | Motor | - | - | - | - | - | - | - | - | - | - | 0 |  | 62 | 62 | 62 | 0 | 0 | 0 | 0
[5 empty] | High ovl | -
7 | 0 | Motor | - | - | - | - | - | - | - | - | - | - | 0 |  | 47 | 47 | 47 | 0 | 0 | 0 | 0
[5 empty] | High ovl | -
|  | INTERMEDIATE TOTAL 1 | [15 empty] | 19200 | 22.8 | 22.8 | 22.8
[8 empty] | Output Current | Input Current | Power loss | Weight | Efficiency | Power
[8 empty] | [A] 230V | [A] 380V | [W] | [kg] |  | [VA]
6 | 1 | Transformer TC1 |  |  |  | 1492-K-BASX-0-N | - | 8.3 | 2.6 | 40 | 8 | 0.8 | 1235 | - | 2.6 | 0 | 2.6 | 1235 | 2.6 | 0 | 2.6
7 | 0 | Transformer TC2 |  |  |  | 4AM5242-8JD40-0FA0 | - | 3 | 1.7 | 40 | 8 | 0.8 | 790 | - | 1.7 | 1.7 | 0 | 0 | 0 | 0 | 0
8 | 0 | Transformer TC3 |  |  |  | 4AM5242-8JD40-0FA0 | - | 3 | 1.7 | 40 | 8 | 0.8 | 790 | - | 1.7 | 0 | 1.7 | 0 | 0 | 0 | 0
9 | 0 | Transformer TC4 |  |  |  | 4AM5242-8JD40-0FA0 | - | 3 | 1.7 | 40 | 8 | 0.8 | 790 | - | 0 | 1.7 | 1.7 | 0 | 0 | 0 | 0
[18 empty] | 1235 | 2.6 | 0 | 2.6
INTERMEDIATE TOTAL 2
[8 empty] | Output Current | Input Current | Power loss | Weight | Efficiency | Power
[8 empty] | [A] 24VDC | [A] 400V | [W] | [kg] |  | [VA]
10 | 0 | 24VDC POWER SUPPLY GS1 |  |  |  | 6EP1434-2BA20 | - | 10 | 0.7 | 23 | 1 | 0.9 | 540 |  | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 0
11 | 0 | 24VDC POWER SUPPLY GS2 |  |  |  | 6EP1434-2BA20 | - | 10 | 0.7 | 23 | 1 | 0.9 | 540 |  | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 0
|  | INTERMEDIATE TOTAL 3 | [15 empty] | 0 | 0 | 0 | 0
|  | INTERMEDIATE TOTAL 1+2+3 | [15 empty] | 20435 | 25.4 | 22.8 | 25.4
12 |  | TOTAL (+20% SPARE INCLUDED) | [15 empty] | 24522 | 30.48 | 27.36 | 30.48
CHOIX 32A

## WEIGHT&HEATING LOSS
|  |  | PANEL 51 |  |  | PANEL 52 |  |  | PANEL 53 |  |  | PANEL 54
| [Kg] | [W] | Qty | Weight [kg] | Heat loos[W] | Qty | Weight [kg] | Heat loos[W] | Qty | Weight [kg] | Heat loos[W] | Qty | Weight [kg] | Heat loos[W]
PANEL
PANEL 800X1800X500 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PANEL 800X1800X600 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PANEL 800X2000X500 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PANEL 1000X2000X500 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PANEL 1000X2000X600 | 160 | 0 | 1 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PANEL 1200X2000X500 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PANEL 1200X2000X600 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0
|  |  | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0
SIDE PANEL 1800X500 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SIDE PANEL 2000X500 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLINTH 800X500X200 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLINTH 800X600X200 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLINTH 800X500X100 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLINTH 1000X500X200 | 12 | 0 | 1 | 12 | 0 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLINTH 1000X500X100 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLINTH 1200X500X200 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLINTH 1200X500X100 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FILTER | 2 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0
FAN | 3.5 | 2 | 1 | 3.5 | 2 | 1 | 3.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0
LED LAMP | 0.5 | 1 | 1 | 0.5 | 1 | 1 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Panel mounting acc ( Rail, screw, lift ring,..) | 15 | 0 | 1 | 15 | 0 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wiring acc ( Distrib,terminal,wiring) | 10 | 10 | 1 | 10 | 10 | 1 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0
DISTRIBUTION
TRAFO 630VA/CB ( 1XIN-2XOUT) | 9 | 100 | 1 | 9 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TRAFO 630VA/CB ( IN-OUT) | 15 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PS 1X230VAC /DC (50W) -CB( 1x IN-OUT) | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PS 1X230VAC /DC (100W) -CB( 1x IN-OUT) | 2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER SUPPLY 3X400VAC /DC (240W) | 1 | 24 | 1 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BUSBAR DISTRIBUTION SYSTEM / 1000A | 21 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CIRCUIT BREAKER 3P-1000A6 ACC | 5 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CTRL
SIMATIC S7 ( PS&CPU&4xIO&RACK) | 8 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCM3P +acc | 8 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCM3F | 8 | 10 | 4 | 32 | 40 | 4 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0
SDU Console | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
RELAY (1..4P)-24VDC | 0.06 | 0.01 | 20 | 1.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DRIVE
Power unit ( Inverter-CB-contactor-A20 Modul
Inverter ( SINAMICS G120, ATV3X, ACS880) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 0,75" " KW | 3 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 1,1" " KW | 3 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 1,5" " KW | 3 | 68 | 0 | 0 | 0 | 4 | 12 | 272 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 2,2" " KW | 3 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 3" " KW | 3 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 4" " KW | 4.5 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 5,5" " KW | 4.5 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 7,5" " KW | 4.5 | 269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 11" " KW | 9 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 15" " KW | 9 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 18,5" " KW |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 22" " KW |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 30" " KW | 21 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 45" " KW | 22 | 1060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 55" " KW | 22 | 1700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 75" " KW |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 90" " KW |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 110" " KW |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 132" " KW |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 160" " KW |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter size" " 200" " KW | 10 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power unit ( Soft starter-CB-contactor-A20 Modul
Inverter (ATS,SIRIUSRW)
Soft starter" " 110" " KW | 18 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100..3500W
LINE REACTOR | 2 | 20 | 4 | 8 | 80 | 4 | 32 | 320
TOTAL |  |  |  | 254.2 | 258.2 |  | 120 | 647 |  | 0 | 0 |  | 0 | 0
|  | Total weight 51+52 |  | 374.2
|  | Total Heat dispation |  | 905.2
CUBICLE (800x1000x400)HEATING DISIPATION | [6 empty] | PANEL (800x2000x500) ( BIGGER SIZE OK-> BIGGER SURFACE)
Climate control calculation with Therm 6.6 | [6 empty] | Climate control calculation with Therm 6.6
Project: Standard | [6 empty] | Project: Standard
Company: NN | [6 empty] | Company: NN
Contact person: NN | [6 empty] | Contact person: NN
Originator: NN | [6 empty] | Originator: NN
Telephone / Fax: NN | [6 empty] | Telephone / Fax: NN
Ambient parameters | [6 empty] | Ambient parameters
Maximum temperature outside the enclosure Ta: 35°C | [6 empty] | Maximum temperature outside the enclosure Ta: 35°C
Maximum temperature inside the enclosure Ti: 40°C | [6 empty] | Maximum temperature inside the enclosure Ti: 40°C
Mains voltage: 400 V including 230 V | [6 empty] | Mains voltage: 400 V including 230 V
Frequency: 50 Hz | [6 empty] | Frequency: 50 Hz
_________________________________________________________ | [6 empty] | _________________________________________________________
Climate control calculation
Enclosure element no. 1
AX 1181000 | [6 empty] | VX 8805000
Width x Height x Depth: 800 x 1000 x 400 mm | [6 empty] | Width x Height x Depth: 800 x 2000 x 500 mm
k-factor of the enclosure: 5,5 | [6 empty] | k-factor of the enclosure: 5,5
Type of installation site: Single enclosure for wall mounting | [6 empty] | Type of installation site: Single enclosure for wall mounting
Average enclosure temperature without climate control: 47°C | [6 empty] | Average enclosure temperature without climate control: 55 °C
Climate control necessary: Yes | [6 empty] | Climate control necessary: Yes
Cooling unit required: No | [6 empty] | Cooling unit required: No
1 x Addition: 150 W | [6 empty] | 1 x Addition: 500 W
Heat loss: 150 W | [6 empty] | Heat loss: 500 W
Heat exchange across surface: 63 W | [6 empty] | Heat exchange across surface: 127 W
Heat to be dissipated: 87 W | [6 empty] | Heat to be dissipated: 373 W
Measures to maintain the temperature | [6 empty] | Measures to maintain the temperature
| Wall-mounted units | Roof-mounted units | [5 empty] | Wall-mounted units | Roof-mounted units
1. Fan-and-filter units | SK3239100 + SK3239200 | [5 empty] | 1. Fan-and-filter units | 2 SK3240100 + 2 SK3240200 |  |  |  | SK32401000 = 230m3/h -> OK ~= 254m3/h
| (87 [m3/h]) | [6 empty] | (276 [m3/h])
| Necessary air throughput: 59 [m3/h] | [6 empty] | Necessary air throughput: 254 [m3/h]

## 24VDC-120VAC CONSUMER
120VAC CONSUMER
Qty | Component | Inrush power / Inrush current | hold-in power | Heating loss | CB Current-Curve | Total hold-in power | Total Heating loss
|  | [VA] / [A] | [VA] | [W] | [A]-.. | [VA] | [W]
0 | Contactor 6A | 30 /- | 4.5 | 0 | - | 0 | 0
0 | Contactor 9A | 70/- | 7 | 0 | - | 0 | 0
0 | Contactor 18A | 70/- | 7 | 0 | - | 0 | 0
0 | Contactor 25A | 70/- | 7 | 0 | - | 0 | 0
0 | Contactor 32A | 70/- | 7 | 0 | - | 0 | 0
0 | Contactor 40A | 160/- | 15 | 0 | - | 0 | 0
0 | Contactor 50A | 160/- | 15 | 0 | - | 0 | 0
0 | Contactor 65A | 245/- | 26 | 0 | - | 0 | 0
0 | Contactor 80A | 245/- | 26 | 0 | - | 0 | 0
0 | Contactor 95A | 245/- | 26 | 0 | - | 0 | 0
0 | SCM3 ( 100W) | ../~60 | 150 |  | 2-D | 0 | 0
0 | BFC |  |  |  |  | 0 | 0
0 | WFC |  |  |  |  | 0 | 0
0 | SOUND |  |  |  |  | 0 | 0
0 | S7-115U |  |  |  |  | 0 | 0
1 | Panel fan xxx m3/h |  | 60 |  |  | 60 | 0
2 | Panel led light 5W | - | 20 | 0 |  | 40 | 0
0 | Panel led light 5W | - | 10 | 0 |  | 0 | 0
1 | 24VDC-2,5A ( 60W) Power supply | ../30 | 75 | 8 | 2-D | 75 | 8
0 | 24VDC-5A ( 120W) Power supply | ../30 | 230 | 24 | 2-D | 0 | 0
0 | 24VDC-10A ( 240W) Power supply | ../30 | 345 | 53 | 2-D | 0 | 0
1 | Service Plug |  | 100 | 0 | 1-D ( FI : Optional) | 100 | 0
3 | A20 Ctrl modul | 0 | 0 | 0 |  | 0 | 0
4 | Heating motor | 30 | 30 | 0 |  | 120 | 0
25 | Relay | 3 | 3 | 0 |  | 75 | 0
| TOTAL |  |  |  |  | 470 | 8
| Spare |  |  |  |  | 30%
| TOTAL |  |  |  |  | 611 | 8
[5 empty] | CHOIX : 1KVA | 1492-K-BASX-0-N
24VDC CONSUMER
Qty | Component | Inrush power / Inrush current | hold-in power | Heating loss | CB Current-Curve | Total hold-in power | Total Heating loss
|  | [VA] / [A] | [W] | [W] | [A]-.. | [W] | [W]
12 | Relay DPDT | - | 1 | 0 | - | 12 | 0
0 | Safety relay ( 4...6xNO) |  | 3 | 0 | - | 0 | 0
0 | Relay SPDT | - | 0.26 | 0 | - | 0 | 0
5 | Signaling lamp | - | 0 | 0 | - | 0 | 0
0 | I/O WAGO | - | 0 | 0 | - | 0 | 0
0 | CPU WAGO | - | 0 | 0 | - | 0 | 0
0 | CPU S7 | - | 0 | 0 | - | 0 | 0
0 | TYPICAL DIGITAL INPUT ( PLC-WGO) | - | 0 | 0 | - | 0 | 0
0 | TYPICAL ANALOG INPUT ( PLC-WGO) | - | 0 | 0 | - | 0 | 0
0 | TYPICAL ANALOG INPUT ( PLC-WGO) | - | 0 | 0 | - | 0 | 0
0 | 24VDC SENSOR WITH EXTERNAL POWER | - | 0 | 0 | - | 0 | 0
2 | PDU Console with ext power | 0 | 5 | 0 |  | 10 | 0
3 | Ethernet Switch | 0 | 5 | 0 |  | 15 | 0
0 | Other device 1 | 0 | 0 | 0 |  | 0 | 0
0 | Other device 2 | 0 | 0 | 0 |  | 0 | 0
0 | Other device 3 | 0 | 0 | 0 |  | 0 | 0
| TOTAL |  |  |  |  | 37 | 0
| Spare |  |  |  |  | 20%
| TOTAL |  |  |  |  | 44.4 | 0
[5 empty] | 24VDC-2,5A ( 60W) Power supply | x
24VDC-5A ( 120W) Power supply
24VDC-10A ( 240W) Power supply

## ANNEX MOTOR
Motor size | Nom Power | Rated Current | Cable gland tape. | Cable gland cap. | Inverter size Heavy duty | Recommanded CB Current[A] | Min cable cross sectionIEC "C"use | Shielded cable 4 cores OD[mm]
| [KW] 400V | [A] 400V |  | [mm] | [KW] 400V | [A] 400V | [mm2]
80M | 0.75 | 1.75 | M25x1,5/M16x1,5 | 13-18/ 5-10 | 1.5 | 6.3 | 2.5 | 2YSLCYK-JB 2,5/OD 12…. | 2.5
90S | 1.1 | 2.55 | M25x1,5/M16x1,5 | 13-18/ 5-10 | 1.5 | 10 | 2.5 | 2YSLCYK-JB 2,5/OD 12…. | 2.5
90L | 1.5 | 3.4 | M25x1,5/M16x1,5 | 13-18/ 5-10 | 2.2 | 10 | 2.5 | 2YSLCYK-JB 2,5/OD 12…. | 2.5
100LS | 2.2 | 4.75 | M32x1,5/M16x1,5 | 18-25/ 5-10 | 3 | 10 | 2.5 | 2YSLCYK-JB 2,5/OD 12…. | 2.5
100L | 3 | 6.4 | M32x1,5/M16x1,5 | 18-25/ 5-10 | 4 | 25 | 2.5 | 2YSLCYK-JB 2,5/OD 12…. | 2.5
112M | 4 | 7.9 | M32x1,5/M16x1,5 | 18-25/ 5-10 | 5.5 | 25 | 2.5 | 2YSLCYK-JB 2,5/OD 12…. | 4
132S | 5.5 | 10.5 | M32x1,5/M16x1,5 | 18-25/ 5-10 | 7.5 | 32 | 4 | 2YSLCYK-JB 2,5/OD 14…. | 6
132M | 7.5 | 15.2 | M32x1,5(2X)/M16x1,5(2X) | 18-25/ 5-10 | 11 | 40 | 6 | 2YSLCYK-JB 2,5/OD 15…. | 10
132L | 9.2 | 18.7 | M32x1,5(2X)/M16x1,5(2X) | 18-25/ 5-10 | 15 | 50 | 10 | 2YSLCYK-JB 10/OD 18… | 16
160M | 11 | 21 | M40x1,5(2X)/M16x1,5(2X) | 24-32/ 5-10 | 15 | 50 | 10 | 2YSLCYK-JB 10/OD 18… | 16
160L | 15 | 29 | M40x1,5(2X)/M16x1,5(2X) | 24-32/ 5-10 | 18.5 | 65 | 16 | 2YSLCYK-JB 10/OD 21… | 25
180M | 18.5 | 33.5 | M40x1,5(2X)/M16x1,5(2X) | 24-32/ 5-10 | 22 | 80 | 16 | 2YSLCYK-JB 16/OD 21… | 25
180L | 22 | 38.5 | M40x1,5(2X)/M16x1,5(2X) | 24-32/ 5-10 | 30 | 110 | 25 | 2YSLCYK-JB 25/OD 27… | 35
200L | 30 | 56 | M50x1,5(2X)/M16x1,5(2X) | 32-38/ 5-10 | 37 | 110 | 25 | 2YSLCYK-JB 25/OD 27… | 50
225S | 37 | 64 | M50x1,5(2X)/M16x1,5(2X) | 32-38/ 5-10 | 45 | 115 | 35 | 2YSLCYK-JB 35/OD 29… | 95
225M | 45 | 81 | M50x1,5(2X)/M16x1,5(2X) | 32-38/ 5-10 | 55 | 150 | 50 | 2YSLCYK-JB 50/OD 34… | 95
250M | 55 | 104 | M63x1,5(2X)/M16x1,5(2X) | 37-44/ 5-10 | 75 | 220 | 95 | 2YSLCYK-JB 95/OD 41… | 95
280S | 75 | 143 | M63x1,5(2X)/M16x1,5(2X) | 37-44/ 5-10 | 90 | 220 | 95 | 2YSLCYK-JB 95/OD 41… | 150
280M | 90 | 161 | M63x1,5(2X)/M16x1,5(2X) | 37-44/ 5-10 | 110 | 220 | 95 | 2YSLCYK-JB 95/OD 41… | 300 ( 2X150)
315S | 110 | 189 | M63x1,5(2X)/M16x1,5(2X) | 37-44/ 5-10 | 132 | 320 | 150 | 2YSLCYK-JB 150/OD 56… | 300 ( 2X150)
315M | 132 | 230 | M63x1,5(2X)/M16x1,5(2X) | 37-44/ 5-10 | 160 | 500 | 300 ( 2X150) | …. | 300 ( 2X150)
315L | 160 | 275 | M63x1,5(2X)/M16x1,5(2X) | 37-44/ 5-10 | 200 | 500 | 300 ( 2X150) | ….
315H | 200 | 355 | M63x1,5(2X)/M16x1,5(2X) | 37-44/ 5-10 | 250 | 500 | 300 ( 2X150) | ….
DESIGN
LUBRICATION
DUTY
EFFICIENCY
Cooling
INSULATION & DERATING ( ALT&TEMP)
DEGREE OF PROTECTION & PAINTING
STARTING METHOD
MOUNTING
STARTING METHOD
VOLTAGE & TOLERANCE & DIRECTION OF ROTATION
NORM & STANDARD
SPEED & POWER

## ANNEX WIRING
METRIC EMC CABLE GLAND | METRIC CABLE GLAND
METRIC EMC CABLE GLAND

## ANNEX MOVIMOT
|  | Nominal Power [kw] Normal Duty | Output voltage [V]/Freq.[Hz] | Input voltage [V]/Freq.[Hz] | Apparerent Power [kVA] Normal Duty | Input current(400V) [A] Normal Duty | Recommanded Circuit breaker
[7 empty] | Nominal current [A] | Icc Rate[kA]
MM03 D-503-00 | 18215076 | 0.37 | 350..550/ 2..120 | 350..550/47..63 | 1.1 | 1.3 | 4 | 100 | LINE FUSE 16A(2,5 mm2)
MM05 D-503-00 | 18215009 | 0.55 | 350..550/ 2..120 | 350..550/47..63 | 1.4 | 1.6 | 4 | 100
MM07 D-503-00 | 18215017 | 0.75 | 350..550/ 2..120 | 350..550/47..63 | 1.8 | 1.9 | 6.3 | 100
MM11 D-503-00 | 18215025 | 1.1 | 350..550/ 2..120 | 350..550/47..63 | 2.2 | 2.4 | 6.3 | 100
MM15 D-503-00 | 18215033 | 1.5 | 350..550/ 2..120 | 350..550/47..63 | 2.8 | 3.5 | 10 | 100
MM22 D-503-00 | 18215041 | 2.2 | 350..550/ 2..120 | 350..550/47..63 | 3.8 | 5 | 14 | 100
MM30 D-503-00 | 18215068 | 3 | 350..550/ 2..120 | 350..550/47..63 | 5.1 | 6.7 | 25 | 100
MM40 D-503-00 | 18215076 | 4 | 350..550/ 2..120 | 350..550/47..63 | 6.7 | 7.3 | 25 | 100
Wiring
E
[8 empty] | 0.37 | 0.55 | 0.75 | 1.1 | 1.5 | 2.2 | 3 | 4
[8 empty] | 80M.. | 90S.. | 80M.. | 90S.. | 90L.. | 100LS.. | 100L.. | 112M..
CONNECTION
[7 empty] | POWER | M25x1,5 | M25x1,5 | M25x1,5 | M25x1,5 | M25x1,5 | M32x1,5 | M32x1,5 | M32x1,5
[7 empty] | CTRL | M16x1,5 | M16x1,5 | M16x1,5 | M16x1,5 | M16x1,5 | M16x1,5 | M16x1,5 | M16x1,5
[7 empty] | SPEED SENSOR | PLUG M16 | PLUG M16 | PLUG M16 | PLUG M16 | PLUG M16 | PLUG M16 | PLUG M16 | PLUG M16
CABLE GLAND
[8 empty] | 1665.9062 | M12x1,5 | CEM/BRASS/IP68 | CE/Ul / CSA | 3,5 ..7mm | SKINTOP MS-SC-M | 53112610
[8 empty] | 1665.9061 | M16x1,5 | CEM/BRASS/IP68 | CE/Ul / CSA | 4,5 ..9mm | SKINTOP MS-SC-M | 53112620
[8 empty] | 1665.9060 | M20x1,5 | CEM/BRASS/IP68 | CE/Ul / CSA | 7 ..12,5mm | SKINTOP MS-SC-M | 53112630
[8 empty] | 1660.5002 | M25x1,5 | CEM/BRASS/IP68 | CE/Ul / CSA | 9..16,5mm | SKINTOP MS-SC-M | 53112640
[8 empty] | 1665.5003 | M32x1,5 | CEM/BRASS/IP68 | CE/Ul / CSA | 11..21mm | SKINTOP MS-SC-M | 53112650
[8 empty] | 1665.5007 | M40x1,5 | CEM/BRASS/IP68 | CE/Ul / CSA | 19..28mm | SKINTOP MS-SC-M | 53112660
BLIND CAP
[8 empty] | 1665.9065 | M12 | CEM/BRASS/IP68 | CE/Ul / CSA | - | SKINTOP | 52103100
[8 empty] | 1665.9064 | M16 | CEM/BRASS/IP68 | CE/Ul / CSA | - | SKINTOP | 52103110
[8 empty] | 1665.9063 | M20 | CEM/BRASS/IP68 | CE/Ul / CSA | - | SKINTOP | 52103120
AMPLIFIER CABLE GLAND
| U/F | [6 empty] | 1665.5034 | M20->M25 | CEM/BRASS/IP68 | CE/Ul / CSA | - | SKINTOP | 52104456
HMI
TACHO CABLE
[10 empty] | OD | 6,6mm
[10 empty] | Conformity | CE/Ul
[10 empty] | IP Rate | 68
[10 empty] | Temp | -25..+60°C
1668.3094
1,5mm2 Max
Ul : N/A
1531.0067
HMI : 2601.9159
CABLE 2602.0001

## ANNEX ATV DRIVE
| Nominal Power [kw] Normal Duty Heavy Duty |  | Output voltage [V]/Freq.[Hz] | Input voltage [V]/Freq.[Hz] | Apparerent Power [kVA] Normal Duty Heavy Duty |  | Input current(400V) [A] Normal Duty Heavy Duty |  | Recommanded Circuit breaker |  |  | Recommanded contactor |  | Wiring cross section [mm2] | Heating loss [W] | Weight [kg] |  |  |  | HIM |  |  |  |  | Price [€]
[9 empty] | Type | Nominal current [A] | Icc Rate[kA] | Type | Nominal current [A] |  |  |  | Width [mm] | Height [mm] | Depth [mm] | NATIV | PLAIN TEXT DISPLAY | GRAPHIC DISPLAY | AQ1 [0..10V,0,4..20mA] | AQ2 [0..10V,0,4..20mA]
ATV340U07N4 | 1.1 | 0.75 | 480/ 599 | 323..528/47..63 | 1.7 | 2.2 | 2.1667 | 2.1667 | GV2L10 | 6.3 | 100 | LC1D09 |  | 2.5 | 49 | 1.7 | 85 | 270 | 233 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U15N4 | 2.2 | 1.5 | 480/ 599 | 323..528/47..63 | 3.4 | 4.1 | 3.8333 | 4.0833 | GV2L14 | 10 | 100 | LC1D09 |  | 2.5 | 69 | 1.7 | 85 | 270 | 233 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U22N4 | 3 | 2.2 | 480/ 599 | 323..528/47..63 | 4.4 | 5.5 | 5.1667 | 5.5 | GV2L16 | 14 | 100 | LC1D12 |  | 2.5 | 90 | 1.8 | 85 | 270 | 233 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U30N4 | 4 | 3 | 480/ 599 | 323..528/47..63 | 5.7 | 7.1 | 6.75 | 7.0833 | GV2L22 | 25 | 100 | LC1D18 |  | 2.5 | 112 | 2.1 | 85 | 270 | 233 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U40N4 | 5.5 | 4 | 480/ 599 | 323..528/47..63 | 7.5 | 8.8 | 9 | 8.8333 | GV2L22 | 25 | 100 | LC1D25 |  | 2.5 | 136 | 2.2 | 85 | 270 | 233 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U55N4 | 7.5 | 5.5 | 480/ 599 | 323..528/47..63 | 10.1 | 13.3 | 12.0833 | 13.3333 | GV2L32 | 32 | 100 | LC1D32 |  | 2.5 | 196 | 2.9 | 110 | 270 | 234 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U75N4 | 11 | 7.5 | 480/ 599 | 323..528/47..63 | 14.7 | 17 | 17.0833 | 17 | GV3L40 | 40 | 100 | LC1D38 |  | 2.5 | 256 | 3 | 110 | 270 | 234 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340D11N4 | 15 | 11 | 480/ 599 | 323..528/47..63 | 19.1 | 23 | 22.75 | 23.0833 | GV3L50 | 50 | 100 | LC1D50 |  | 10 | 313 | 9.5 | 180 | 385 | 249 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340D15N4 | 18.5 | 15 | 480/ 599 | 323..528/47..63 | 25.1 | 29.7 | 28.3333 | 29.75 | GV3L65 | 65 | 100 | LC1D65 |  | 10 | 443 | 9.5 | 180 | 385 | 249 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340D18N4 | 22 | 18.5 | 480/ 599 | 323..528/47..63 | 29.1 | 36.1 | 33.5 | 36.1667 | GV3L80 | 80 | 100 | LC1D80 |  | 16 | 559 | 10.2 | 180 | 385 | 249 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340D22N4 | 30 | 22 | 480/ 599 | 323..528/47..63 | 40.4 | 42.1 | 45.25 | 42.1667 | NSX100 | 110 | 100 | LC1D95 |  | 10 | 680 | 10.2 | 180 | 385 | 249 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U07N4E | 1.1 | 0.75 | 480/ 599 | 323..528/47..63 | 1.7 | 2.2 | 2.1667 | 2.1667 | GV2L10 | 6.3 | 100 | LC1D09 |  | 2.5 | 49 | 1.7 | 85 | 270 | 233 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U15N4E | 2.2 | 1.5 | 480/ 599 | 323..528/47..63 | 3.4 | 4.1 | 3.8333 | 4.0833 | GV2L14 | 10 | 100 | LC1D09 |  | 2.5 | 69 | 1.7 | 85 | 270 | 233 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U22N4E | 3 | 2.2 | 480/ 599 | 323..528/47..63 | 4.4 | 5.5 | 5.1667 | 5.5 | GV2L16 | 14 | 100 | LC1D12 |  | 2.5 | 90 | 1.8 | 85 | 270 | 233 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U30N4E | 4 | 3 | 480/ 599 | 323..528/47..63 | 5.7 | 7.1 | 6.75 | 7.0833 | GV2L22 | 25 | 100 | LC1D18 |  | 2.5 | 112 | 2.1 | 85 | 270 | 233 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U40N4E | 5.5 | 4 | 480/ 599 | 323..528/47..63 | 7.5 | 8.8 | 9 | 8.8333 | GV2L22 | 25 | 100 | LC1D25 |  | 2.5 | 136 | 2.2 | 85 | 270 | 233 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U55N4E | 7.5 | 5.5 | 480/ 599 | 323..528/47..63 | 10.1 | 13.3 | 12.0833 | 13.3333 | GV2L32 | 32 | 100 | LC1D32 |  | 4 | 196 | 2.9 | 110 | 270 | 234 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340U75N4E | 11 | 7.5 | 480/ 599 | 323..528/47..63 | 14.7 | 17 | 17.0833 | 17 | GV3L40 | 40 | 100 | LC1D38 |  | 6 | 256 | 3 | 110 | 270 | 234 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340D11N4E | 15 | 11 | 480/ 599 | 323..528/47..63 | 19.1 | 23 | 22.75 | 23.0833 | GV3L50 | 50 | 100 | LC1D50 |  | 10 | 313 | 9.5 | 180 | 385 | 249 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340D15N4E | 18.5 | 15 | 480/ 599 | 323..528/47..63 | 25.1 | 29.7 | 28.3333 | 29.75 | GV3L65 | 65 | 100 | LC1D65 |  | 16 | 443 | 9.5 | 180 | 385 | 249 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340D18N4E | 22 | 18.5 | 480/ 599 | 323..528/47..63 | 29.1 | 36.1 | 33.5 | 36.1667 | GV3L80 | 80 | 100 | LC1D80 |  | 16 | 559 | 10.2 | 180 | 385 | 249 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340D22N4E | 30 | 22 | 480/ 599 | 323..528/47..63 | 40.4 | 42.1 | 45.25 | 42.1667 | NSX100 | 110 | 100 | LC1D95 |  | 25 | 680 | 10.2 | 180 | 385 | 249 | NO | VW3A1113 | VW3A1111 | Nativ | None
ATV340D30N4E | 37 | 30 | 480/ 599 | 323..528/47..64 |  |  | 47.75 | 40.25 | NSX100 | 110 | 100 | LC1D95 |  | 25 | 661 | 27.9 | 212 | 660 | 262 | NO | VW3A1113 | VW3A1111 | Nativ | Nativ
ATV340D37N4E | 45 | 37 | 480/ 599 | 323..528/47..65 |  |  | 57.5833 | 49.1667 | GV4L115B | 115 | 100 | LC1D115 |  | 35 | 780 | 28.4 | 212 | 660 | 262 | NO | VW3A1113 | VW3A1111 | Nativ | Nativ
ATV340D45N4E | 55 | 45 | 480/ 599 | 323..528/47..66 |  |  | 70.1667 | 59.8333 | GV4L115B | 115 | 100 | LC1D115 |  | 50 | 776 | 56.4 | 271 | 908 | 309 | NO | VW3A1113 | VW3A1111 | Nativ | Nativ
ATV340D55N4E | 75 | 55 | 480/ 599 | 323..528/47..67 |  |  | 93.9167 | 72.4167 | NSX160 | 150 | 100 | LC1D150 |  | 95 | 987 | 57.9 | 271 | 908 | 309 | NO | VW3A1113 | VW3A1111 | Nativ | Nativ
ATV340D75N4E | 90 | 75 | 480/ 599 | 323..528/47..68 |  |  | 113.1667 | 98.4167 | NSX250 | 220 | 100 | LC1F225 |  | 95 | 1364 | 58.4 | 271 | 908 | 309 | NO | VW3A1113 | VW3A1111 | Nativ | Nativ
ATV930U07N4 | 0.75 | 0.37 | 480/ 599 | 323..528/47..68 | [12 empty] | 144 | 350 | 206
ATV930U15N4 | 1.5 | 0.75 | 480/ 599 | 323..528/47..68 | [12 empty] | 144 | 350 | 206
ATV930U22N4 | 2.2 | 1.5 | 480/ 599 | 323..528/47..68 | [12 empty] | 144 | 350 | 206
ATV930U30N4 | 3 | 2.2 | 480/ 599 | 323..528/47..68 | [12 empty] | 144 | 350 | 206
ATV930U40N4 | 4 | 3 | 480/ 599 | 323..528/47..68 | [12 empty] | 144 | 350 | 206
ATV930U55N4 | 5.5 | 4 | 480/ 599 | 323..528/47..68 | [12 empty] | 144 | 350 | 206
ATV930U75N4 | 7.5 | 5.5 | 480/ 599 | 323..528/47..68 | [12 empty] | 171 | 409 | 236
ATV930D11N4 | 11 | 7.5 | 480/ 599 | 323..528/47..68 | [12 empty] | 171 | 409 | 236
ATV930D15N4 | 15 | 11 | 480/ 599 | 323..528/47..68 | [12 empty] | 211 | 545 | 235
ATV930D18N4 | 18.5 | 15 | 480/ 599 | 323..528/47..68 | [12 empty] | 211 | 545 | 235
ATV930D22N4 | 22 | 18.5 | 480/ 599 | 323..528/47..68 | [12 empty] | 211 | 545 | 235
ATV930D30N4 | 30 | 22 | 480/ 599 | 323..528/47..68 | [12 empty] | 226 | 673 | 274
ATV930D37N4 | 37 | 30 | 480/ 599 | 323..528/47..68 | [12 empty] | 226 | 673 | 274
ATV930D45N4 | 45 | 37 | 480/ 599 | 323..528/47..68 | [12 empty] | 226 | 673 | 274
ATV930D55N4 | 55 | 45 | 480/ 599 | 323..528/47..68 | [12 empty] | 290 | 922 | 325
ATV930D75N4 | 75 | 55 | 480/ 599 | 323..528/47..68 | [12 empty] | 290 | 922 | 325
ATV930D90N4 | 90 | 75 | 480/ 599 | 323..528/47..68
ATV930C11N4 | 110 | 90 | 480/ 599 | 323..528/47..68 |  |  |  |  | NSX250 | 220 | 100 | LC1F225 |  | 95 |  |  | 320 | 1205 | 393
ATV930C13N4 | 132 | 110 | 480/ 599 | 323..528/47..68 |  |  |  |  | NSX250 | 220 | 100 | LC1F225 |  | 150 |  |  | 320 | 1205 | 393
ATV930C16N4 | 160 | 132 | 480/ 599 | 323..528/47..68 |  |  |  |  | NSX400 | 320 | 100 | LC1G265 |  | 300 ( 2X150) |  |  | 320 | 1205 | 393
ATV930C22N4 | 220 | 160 | 480/ 599 | 323..528/47..68 |  |  |  |  | NSX630 | 500 | 100 | LC1G400 |  | 300 ( 2X150) |  |  | 440 | 1195 | 380
ATV930C25N4C | 250 | 200 | 480/ 599 | 323..528/47..68 |  |  |  |  | NSX630 | 500 | 100 | LC1G500 |  | 300 ( 2X150) |  |  | 440 | 1195 | 380
DUTY
|  |  |  | ND | HD |  | SONEPAR |  |  |  |  | SONEPAR
[7 empty] | INVERTER | HMI | TOTAL | SCHNEIDER DELIVERY * |  | INVERTER | SCHNEIDER DELIVERY* |  | * WORKING DAY
|  |  |  | 0.75 | 0.37 | [5 empty] | ATV930U07N4 | 518 | 50
|  |  |  | 1.1 | 0.75 | ATV340U07N4E | 476 | 45 | 521 | 20 | - | - | -
|  |  |  | 1.5 | 0.75 | - | - | - | - | - | ATV930U15N4 | 583 | 50
|  |  |  | 2.2 | 1.5 | ATV340U15N4E | 528 | 45 | 573 | 20 | ATV930U22N4 | 661 | 54
|  |  |  | 3 | 2.2 | ATV340U22N4E | 583 | 45 | 628 | 20 | ATV930U30N4 | 754 | 54
|  |  |  | 4 | 3 | ATV340U30N4E | 667 | 45 | 712 | 20 | ATV930U40N4 | 873 | 30
|  |  |  | 5.5 | 4 | ATV340U40N4E | 772 | 45 | 817 | 20 | ATV930U55N4 | 992 | 52
|  |  |  | 7.5 | 5.5 | ATV340U55N4E | 880 | 45 | 925 | 20 | ATV930U75N4 | 1164 | 40
|  |  |  | 11 | 7.5 | ATV340U75N4E | 1050 | 45 | 1095 | 20 | ATV930D11N4 | 1316 | 40
|  |  |  | 15 | 11 | ATV340D11N4E | 1320 | 45 | 1365 | 20 | ATV930D15N4 | 1585 | 40
|  |  |  | 18.5 | 15 | ATV340D15N4E | 1546 | 45 | 1591 | 30 | ATV930D18N4 | 1842 | 40
|  |  |  | 22 | 18.5 | ATV340D18N4E | 1742 | 45 | 1787 | 30 | ATV930D22N4 | 2105 | Not confirmed
|  |  |  | 30 | 22 | ATV340D22N4E | 2091 | 45 | 2136 | 30 | ATV930D30N4 | 2504 | Not confirmed
|  |  |  | 37 | 30 | ATV340D30N4E | 2619 | 45 | 2664 | Not confirmed | ATV930D37N4 | 2970 | Not confirmed
|  |  |  | 45 | 37 | ATV340D37N4E | 3126 | 45 | 3171 | Not confirmed | ATV930D45N4 | 3456 | Not confirmed
|  |  |  | 55 | 45 | ATV340D45N4E | 3607 | 45 | 3652 | Not confirmed | ATV930D55N4 | 4019 | Not confirmed
|  |  |  | 75 | 55 | ATV340D55N4E | 4230 | 45 | 4275 | Not confirmed | ATV930D75N4 | 5547 | Not confirmed
|  |  |  | 90 | 75 | ATV340D75N4E | 5788 | 45 | 5833 | Not confirmed | ATV930D90N4 | 6432 | Not confirmed
|  |  |  | 110 | 90 | - | - | - | - |  | ATV930C11N4 | 7983 | Not confirmed
|  |  |  | 132 | 110 | - | - | - | - |  | ATV930C13N4 | 9084 | 128
|  |  |  | 160 | 132 | - | - | - | - |  | ATV930C16N4 | 10065 | 20
|  |  |  | 220 | 160 | - | - | - | - |  | ATV930C22N4 | 11033 | Not confirmed
|  |  |  | 250 | 200 | - | - | - | - |  | ATV930C25N4C | 12194 | Not confirmed

## ANNEX BUSBAR
BARRE TYPE | Current | Section |  | Cu Resistivity | Barre lenght | Heating loss | Bar Qty | Heating loss tot
|  | [mm2] | [m2] | Ohm m | [m] | [w] |  | [w]
TT 1600A | 1000 | 720 | 0.00072 | 1.6e-08 | 2 | 44.4444 | 3 | 133.3333
Icc : 70kA
700mm support de barre

## SOFT STARTER
[5 empty] | RADIO SPARE | SIEMENS ( BRUT) | SIEMENS ( NET)
POMPE A VIDE
SOFT STARTER
|  | 200KW ( 400/230V) | SOFT STARTER 315A / LINE / PROFISAFE/PNET MOD | 3RW5545-6HF04 & 3RW5980-0CS00 | 7368 | 6557.52 | 5573.892
|  | 3L+PE | SOFT STARTER 364A / LINE / -/PNET | 3RW5545-6HA04& 3RW5980-0CS00 | 6540 | 5820.6 | 4947.51
|  | 200KW ( 690/230V) | SOFT STARTER 210A / DELTA / PROFISAFE/PNET MOD | 3RW5543-6HF04 &3RW5980-0CS00 | 5424 | 4827.36 | 4103.256
|  | 6L+PE | SOFT STARTER 210 / DELTA / -/PNET | 3RW5243-6TC04 &3RW5980-0CS00 | 3700 | 3293 | 2799.05 | -244.5%
VV/VF
|  | 200KW ( 400/230V) | INVERTER : PU: 200KW HO & CPU: PROFISAFE-PNET | 6SL3210-1PE34-8AL0&6SL3244-0BB13-1FA0 | - | 21100 | 14137
3L+PE
POMPE A FILTRAT ( Admis 45KW)
SOFT STARTER
|  | 45KW ( 400/230V) | SOFT STARTER 81A / LINE / PROFISAFE/PNET MOD | 3RW5527-1HF04 & 3RW5980-0CS00 | 3200 | 2848 | 2420.8
|  | 3L+PE | SOFT STARTER 93A / LINE / -/PNET | 3RW5227-1AC05 & 3RW5980-0CS00 | 2100 | 1869 | 1588.65
|  | 45KW ( 690/230V) | SOFT STARTER 81A / DELTA / PROFISAFE/PNET MOD | 3RW5524-1HF04 & 3RW5980-0CS00 | 2376 | 2114.64 | 1797.444
|  | 6L+PE | SOFT STARTER 47A / LINE / -/PNET | 3RW5224-1AC05 & 3RW5980-0CS00 | 1420 | 1263.8 | 1074.23
-90.83%
VV/VF
|  | 45KW ( 400/230V) | INVERTER : PU: 40KW HO & CPU: PROFISAFE-PNET | 6SL3210-1PE31-1AL0&6SL3244-0BB13-1FA0 | - | 4900 | 3430
3L+PE
EU-Code des douanes: 85371098
Origine: CZ
EKN: N
CH-Code des douanes: *
Délai de livraison: 11 semaines

## SAFETY RELAY
|  |  | Supply Voltage | OUTPUT
|  |  |  | SAFETY OUT QTY | SAFETY OUT RATE
SCHNEIDER
| Saftey relay | XPSUAF13AP | 24VDC/DC | 3x NO | 3A -250VAC
|  | XPSUEP14AP | 24DC
| Saftey relay | XPSUAF33AP
XPSUEP34AP